# HARMONIC/INTERHARMONIC COMPUTATION (IEC 61000-4-7)

- Signal processing architecture

- How the DFT is applied

- Harmonic/interharmonic grouping rules

- Real-time buffering and windowing

- Practical considerations in embedded or DSP systems

What IEC 61000-4-7 Defines

IEC 61000-4-7 is a measurement framework that:

- Standardizes harmonic and interharmonic measurement

- Prescribes signal conditioning, window size, and harmonic bin grouping

- Ensures uniform and comparable measurements for power quality analysis

Step-by-Step Real-Time Implementation Guide

Step 1: Signal Acquisition

- Voltage and current signals are acquired using CTs/PTs.

- Sample rate = Typically 12 kHz or 10.24 kHz (should be at least 256 samples per cycle for good resolution).

  - Example: For 50 Hz, 10.24 kHz → 204.8 samples/cycle

- Ensure synchronized acquisition of 3-phase signals (if 3-phase)

Use anti-aliasing filters before digitization.

Step 2: Define the Measurement Window

IEC 61000-4-7 specifies a window of:

- 10 cycles for 50 Hz → 0.2 seconds

- 12 cycles for 60 Hz → 0.2 seconds

So:

- For 50 Hz, at 10.24 kHz sampling:

Samples per window=0.2×10240=2048 samples\text{Samples per window} = 0.2 \times 10240 = 2048 \text{ samples}Samples per window=0.2×10240=2048 samples

You can use:

- Non-overlapping windows → simpler

- Overlapping/rolling windows → smoother output but more compute

For each 0.2s window:

- Store RMS magnitude of each 5 Hz bin

- Tag each bin as harmonic or interharmonic based on center frequency

Step 7: Optional Averaging for Reporting

To smooth noisy values or meet compliance requirements:

- Average harmonic values over 1s, 3s, or 10s

- Rolling average or block average

IEC 61000-4-30 standard recommends:

- 10-minute averages for long-term statistics

- 3-second RMS windows for short-term flicker/harmonic analysis

Step 8: Real-Time Hardware Implementation

Typical real-time platforms:

- DSPs or microcontrollers with:

  - High-speed ADC o 	DMA for buffering

  - FFT accelerators or software DFT routines

- FPGA + ARM SoC systems for more parallelism

- Embedded Linux + RT kernel on SBCs (e.g., BeagleBone, Raspberry Pi)

Data Flow:

[ADC] → [Buffer 0.2s] → [Windowing] → [DFT] → [Group + RMS] → [Harmonic THD Output]

Visualization (Optional)

Plot:

- Harmonic spectrum (bar graph)

- THD vs time (line graph)

- Spectrogram (time-frequency heatmap of harmonics)

Summary: Key Parameters Per IEC 61000-4-7

Parameter 	Value / Rule

Sampling Frequency 	≥ 10 kHz (recommended ≥ 256 samples/cycle)

DFT Window Duration 	0.2 seconds (10 cycles @ 50 Hz)

DFT Frequency Resolution 5 Hz (with 2048 samples @ 10.24 kHz)

Harmonic Group Width 	±2.5 Hz around integer multiples of f₀

THD Formula 	Based on grouped harmonic RMS

# VOLTAGE SAG/SWELL

What are Voltage Sags and Swells?

Event 	Definition

A short-duration decrease in RMS voltage (10%–90% of nominal), lasting from 0.5

Voltage Sag cycles to 1 minute

Voltage 	A short-duration increase in RMS voltage (110%–180% of nominal), for the same time Swell 	range

Typical thresholds:

Real-Time Detection Method (High-Level Flow)

[ ADC Input ] → [ Sliding RMS Computation ] → [ Threshold Comparison ] → [ Event Detection ]

Step-by-Step Real-Time Detection Flow

1. Sample the Voltage Waveform

- High-speed ADC (e.g., 10–20 kHz)

- At least 256–512 samples per cycle for good accuracy

2. Compute RMS over a Sliding Window

4. Detect and Log the Event

If sag/swell condition is detected:

- Log the timestamp

- Record duration of the event

- Capture waveform snippet (pre-fault & post-fault data)

- Trigger alarm or protection if needed

Practical Implementation (Embedded or Real-Time Systems)

Component 	Description

Microcontroller/DSP Performs RMS calculation and threshold comparison

Circular Buffer 	Stores last 1-2 cycles of voltage samples

Interrupt or Timer 	Triggers RMS computation periodically

Event Logger 	Logs event time, magnitude, duration

Example: Detect Sag in Python (Pseudo-Real-Time)

import numpy as np

# Simulation parameters fs = 10240  # 10.24 kHz f_nom = 50 V_nom = 230 cycle_samples = int(fs / f_nom) window_size = cycle_samples  # 1-cycle RMS

# Simulated voltage signal t = np.arange(0, 1, 1/fs) v = V_nom * np.sin(2 * np.pi * f_nom * t) v[5000:7000] *= 0.5  # Introduce a sag

# Real-time-like detection loop for i in range(window_size, len(v)):     window = v[i - window_size:i]

Vrms = np.sqrt(np.mean(window**2))

if Vrms < 0.9 * V_nom:

print(f"SAG at t = {t[i]:.3f}s, Vrms = {Vrms:.1f} V")     elif Vrms > 1.1 * V_nom:

print(f"SWELL at t = {t[i]:.3f}s, Vrms = {Vrms:.1f} V")

Visualization Example

If using GUI or SCADA, plot:

- Voltage waveform

- RMS voltage vs time

- Sag/Swell events as markers

Integration with IEC 61000-4-30

IEC 61000-4-30 defines Power Quality Measurement Methods, including:

- Voltage dip/swell classification

- Duration and magnitude logging

- Aggregation over time intervals (3s, 10min, etc.)

| Summary Table |  |
| --- | --- |
| Task | Real-Time Method |
| Sampling | 10–20 kHz ADC |
| RMS Window | 1-cycle sliding RMS |
| Thresholds | ±10% of nominal |

Detection Frequency Every 5–10 ms

Outputs 	Timestamp, Vrms, Duration, Event Type

# VOLTAGE FLICKER (IEC 61000-4-15)

What Is Flicker?

Flicker is the perceived light intensity variation due to voltage fluctuations, usually from nonlinear or fluctuating loads (e.g., arc furnaces, welders, large motors). Even small voltage modulations (0.5–30 Hz) can make lamps flicker and cause discomfort or irritation.

IEC 61000-4-15: Flickermeter Standard IEC 61000-4-15 defines:

- The architecture of the flickermeter

- Signal processing algorithms to simulate human eye sensitivity

- How to compute:

  - Pst – Short-term flicker severity (10-minute window)

  - Plt – Long-term flicker severity (2-hour window)

Detailed Stage

-

by

-

Stage Breakdown

1 ⃣ Input Conditioning

- Input: Single-phase or 3-phase voltage

- Voltage is scaled to match a nominal lamp voltage (~230 V)

- Anti-aliasing filter applied

- Sampling rate typically ≥ 10 kHz

3

⃣

Weighting Filter

- Models lamp + human eye + brain sensitivity

- It passes modulations between 0.5 – 30 Hz

- Very specific filter with a known transfer function o 	Gain peaks around 8.8 Hz (most sensitive flicker frequency)

This filter emulates how humans perceive flicker: very sensitive to 8.8 Hz voltage modulations!

4 ⃣ Squaring and Smoothing

• 	Output from weighting filter is squared (to relate to power/perception) • 	Then passed through smoothing low-pass filter with specific time constant

The output is a perception-level signal (like “irritation level” over time).

5 ⃣ Statistical Evaluation: Pst and Plt

A. Short-Term Flicker Severity (Pst)

- Computed over 10 minutes

- Based on the cumulative probability distribution of the flicker level signal

- IEC defines percentile values:

o 	P0.1, P1, P3, P10, P50

TYPICAL LIMITS

- Pst ≤ 1.0 is typically acceptable (under IEC or utility grid code)

- Plt ≤ 0.8 is stricter for long-term flicker

| Real-Time Implementation Summary |  |  |
| --- | --- | --- |
| Stage | Task | Notes |
| Preprocessing | Scale, Filter, Normalize | ≥ 10kHz sampling |
| Envelope Detection | Extract voltage modulation | Use rectifier or Hilbert transform |
| Weighting Filter | Apply frequency sensitivity | Digital IIR filter |
| Smoothing | Low-pass filtered squaring | Time constant ~300 ms |
| Stats Engine | Build 10-min histogram, compute Pst | Save output every 10 minutes |

Tools to Build a Flickermeter

In MATLAB/Python:

- Use digital filters (IIR, FIR) to model each stage

- Use RMS envelope or Hilbert transform

- Collect 10 min worth of data → percentiles → compute Pst

In Embedded Systems:

- Use circular buffer for 10-minute data window

- Precomputed IIR filter coefficients for weighting filter

- Fixed-point arithmetic (for resource efficiency)

Output Example

Time: 14:00:00

Pst: 0.76

Plt: 0.64

Limit Compliance: PASS

Integration in PQ Systems

Combine this flickermeter block with:

- Harmonic DFT (IEC 61000-4-7)

- RMS/Voltage Sag/Swell (IEC 61000-4-30)

- Event Logger

- GPS-timestamped logs